## Slide 1
Prairie Island
Site Survey
June 6-7, 2022

## Slide 2: Prairie Island Site Survey - Summary
399 Points we can read – approximately 50% of Operator Rounds
  168 Gauges with Needles (use Wireless Gauge Reader to read)
    128 standard gauges, standard installation
    11 need to tape tail of needle
    18 need to remove sticker from under glass
    1 with loose glass
    9 are high up – need Ops concurrence to install
  22 Numeric Displays (use Wireless Digit Reader to read)
    19 standard displays, standard installation
    3 have displays off or not always on
  153 Indicator Lights (use Indicator Light WTR to read)
  6 Thermometers (use WHTM as ambient thermometer)
  50 Calculated Values (values calculated from instrument readings)

## Slide 3: Prairie Island Site Survey - Summary
Points we cannot read:
  Visual check of room/surrounding area
  Requires operator to push button/actuate/test
  Tubes
  Sight glasses
  Controller panels (e.g. air compressor control panel)

## Slide 4: Budgetary Quote
One Year Parts and Labor Warranty Included
Suggest to budget $70,000 per year annual maintenance starting year 2
NRE to install GBC application on Xcel Windows Server per Nick’s request.

## Slide 5: Background Details

## Slide 6: Prairie Island Site Survey - Summary
399 Points we can read – about 50% of Operator Rounds
  168 Gauges with Needles (use Wireless Gauge Reader to read)
    128 standard gauges, standard installation
    11 need to tape tail of needle
    18 need to remove sticker from under glass
    1 with loose glass
    9 are high up – need Ops concurrence to install
  22 Numeric Displays (use Wireless Digit Reader to read)
    19 standard displays, standard installation
    3 have displays off or not always on
  153 Indicator Lights (use Indicator Light WTR to read)
  6 Thermometers (use WHTM as ambient thermometer)
  50 Calculated Values (values calculated from instrument readings)

## Slide 7: Gauges with Needles - examples

## Slide 8: Gauges with Needles – Need to tape tail
Needle same width head and tail
Open glass, taped tail

## Slide 9: Gauges with Needles – Remove sticker
Open glass lens, remove sticker, replace glass lens

## Slide 10: Gauges with Needles – High Location
Check with Ops to see if OK to cover gauge with WGR

## Slide 11: Prairie Island Site Survey - Summary
399 Points we can read – about 50% of Operator Rounds
  168 Gauges with Needles (use Wireless Gauge Reader to read)
    128 standard gauges, standard installation
    11 need to tape tail of needle
    18 need to remove sticker from under glass
    1 with loose glass
    9 are high up – need Ops concurrence to install
  22 Numeric Displays (use Wireless Digit Reader to read)
    19 standard displays, standard installation
    3 have displays off or not always on
  153 Indicator Lights (use Indicator Light WTR to read)
  6 Thermometers (use WHTM as ambient thermometer)
  50 Calculated Values (values calculated from instrument readings)

## Slide 12: Numeric Displays - examples
Display off unless chiller unit turned-on

## Slide 13: Prairie Island Site Survey - Summary
399 Points we can read – about 50% of Operator Rounds
  168 Gauges with Needles (use Wireless Gauge Reader to read)
    128 standard gauges, standard installation
    11 need to tape tail of needle
    18 need to remove sticker from under glass
    1 with loose glass
    9 are high up – need Ops concurrence to install
  22 Numeric Displays (use Wireless Digit Reader to read)
    19 standard displays, standard installation
    3 have displays off or not always on
  153 Indicator Lights (use Indicator Light WTR to read)
  6 Thermometers (use WHTM as ambient thermometer)
  50 Calculated Values (values calculated from instrument readings)

## Slide 14: Indicator Lights - examples

## Slide 15: Prairie Island Site Survey - Summary
399 Points we can read – about 50% of Operator Rounds
  168 Gauges with Needles (use Wireless Gauge Reader to read)
    128 standard gauges, standard installation
    11 need to tape tail of needle
    18 need to remove sticker from under glass
    1 with loose glass
    9 are high up – need Ops concurrence to install
  22 Numeric Displays (use Wireless Digit Reader to read)
    19 standard displays, standard installation
    3 have displays off or not always on
  153 Indicator Lights (use Indicator Light WTR to read)
  6 Thermometers (use WHTM as ambient thermometer)
  50 Calculated Values (values calculated from instrument readings)

## Slide 16: Prairie Island Site Survey - Summary
399 Points we can read – about 50% of Operator Rounds
  168 Gauges with Needles (use Wireless Gauge Reader to read)
    128 standard gauges, standard installation
    11 need to tape tail of needle
    18 need to remove sticker from under glass
    1 with loose glass
    9 are high up – need Ops concurrence to install
  22 Numeric Displays (use Wireless Digit Reader to read)
    19 standard displays, standard installation
    3 have displays off or not always on
  153 Indicator Lights (use Indicator Light WTR to read)
  6 Thermometers (use WHTM as ambient thermometer)
  50 Calculated Values (values calculated from instrument readings)

## Slide 17: Thermometers - examples

## Slide 18
Detail by Operator Round Sequence
and Instrument

## Slide 19
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 2
Tag: 70450
Type: Light
Count: 20
Possible: Yes
Comments:
Filename: 20220606_115123+seq2!70450.jpg
20220606_115128+seq2!70450.jpg

## Slide 20
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 6
Tag: 12123
Type: Gauge
Count: 1
Possible: Yes*
Comments: Tape Tail
Filename: 20220606_115504+seq6!12123.jpg
20220606_115521+seq7!11209.jpg
20220606_115531+seq7!11209.jpg

## Slide 21
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 7
Tag: 11209
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_115622+seq7!11209.jpg

## Slide 22
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 8
Tag: 11210
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_115714+seq8!11210.jpg

## Slide 23
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 10
Tag: 11213
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_115837+seq10!11213.jpg

## Slide 24
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 11
Tag: 11194
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_115901+seq11!11194.jpg

## Slide 25
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 12
Tag: 11195
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_115911+seq12!11195.jpg

## Slide 26
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 14
Tag: 12114
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_120036+seq14!12114.jpg

## Slide 27
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 15
Tag: 12115
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_120038+seq15!12115.jpg

## Slide 28
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 16
Tag: 12116
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_120104+seq16!12116.jpg

## Slide 29
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 17
Tag: 12119
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_120107+seq17!12119.jpg

## Slide 30
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 18
Tag: 12117
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_120119+seq18!12117.jpg

## Slide 31
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 19
Tag: 12118
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_120122+seq19!12118.jpg

## Slide 32
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 20
Tag: 12120
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_120221+seq20!12120.jpg

## Slide 33
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 21
Tag: 12121
Type: Gauge
Count: 1
Possible: Yes*
Comments: Tape Tail
Filename: 20220606_120233+seq21!12121.jpg

## Slide 34
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 22
Tag: 12122
Type: Gauge
Count: 1
Possible: Yes*
Comments: Tape Tail
Filename: 20220606_120416+seq22!12122.jpg

## Slide 35
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 25
Tag: Victoreen
Type: Light
Count: 16
Possible: Yes*
Comments:
Verify Mount
Filename: 20220606_120652+seq25!Victoreen.jpg

## Slide 36
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 26
Tag: GRP.SEL
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_120812+seq26!GRP.SEL.jpg

## Slide 37
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 27
Tag: GP-2
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_120824+seq27!GP-2.jpg

## Slide 38
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 28
Tag: GP-1
Type: Light
Count: 1
Possible: Yes
Comments:
Filename:
20220606_120830+seq28!GP-1.jpg
20220606_120853+seq29!GP-1.jpg

## Slide 39
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 30
Tag: Victoreen
Type: Light
Count: 4
Possible: Yes
Comments:
Filename: 20220606_121604+seq30!Light.jpg

## Slide 40
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 32
Tag: 18435
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_121823+seq32!18435.jpg

## Slide 41
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 36
Tag: 2603
Type: Thermometer
Count: 1
Possible: Yes*
Comments: WHTM
Filename: 20220606_122050+seq36!Thermometer.jpg

## Slide 42
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 37
Tag: PLC-ON
Type: Light
Count: 2
Possible: No
Comments:
Blinking Light
Filename: 20220606_122141+seq37.jpg

## Slide 43
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 41
Tag: 26022
Type: Thermometer
Count: 1
Possible: Yes*
Comments:
WHTM
Filename: 20220606_122329+seq41!26022.jpg

## Slide 44
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 44
Tag: PLC-ON
Type: Light
Count: 1
Possible: No
Comments:
Blinking Light
Filename: 20220606_122539+seq44!PLC-ON.jpg

## Slide 45
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 47
Tag: 26024
Type: Thermometer
Count: 1
Possible: Yes*
Comments: WHTM
Filename: 20220606_122601+seq41!26024.jpg

## Slide 46
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 49
Tag: 26021
Type: Gauge
Count: 1
Possible: Yes*
Comments: WHTM
Filename: 20220606_122705+seq41!26021.jpg

## Slide 47
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 52
Tag: 81A/B11
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_122846.jpg
20220606_122913.jpg
20220606_122916.jpg
20220606_122930.jpg

## Slide 48
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 53
Tag: 81B/B11
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_122844.jpg

## Slide 49
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 54
Tag: 81A/B12
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_122851.jpg

## Slide 50
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 55
Tag: 81B/B12
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_122849.jpg

## Slide 51
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 56
Tag: 17734
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_123033seq56!17734.jpg

## Slide 52
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 57
Tag: 17733
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_123044+seq57!17733.jpg

## Slide 53
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 59
Tag: 1481
Type: Tube
Count: 1
Possible: No
Comments:
Filename: 20220606_123129+seq59!1481.jpg

## Slide 54
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 59
Tag: 1481
Type: Tube
Count: 1
Possible: No
Comments:
Filename: 20220606_123131+seq59!1481.jpg

## Slide 55
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 60
Tag: 39040
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_123229+seq60!39040.jpg

## Slide 56
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 61
Tag: 11085
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_123325seq61!11085.jpg

## Slide 57
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 62
Tag: 11459
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker behind glass
Filename: 20220606_123348seq62!11459.jpg

## Slide 58
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 63
Tag: 11588
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_123522+seq63!11588.jpg

## Slide 59
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 64
Tag: 16411
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_123601+seq64!16411.jpg

## Slide 60
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 78
Tag: 28994
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_124040seq78!AutoLight.jpg

## Slide 61
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 79
Tag: LockedLight
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_124052+seq79!LockedLight.jpg

## Slide 62
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 80
Tag: Mel Operated
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_124057+seq80toseq84!NotLit.jpg

## Slide 63
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 81
Tag: OEL Operated
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_124057+seq80toseq84!NotLit.jpg

## Slide 64
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 82
Tag: VFL Operated
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_124057+seq80toseq84!NotLit.jpg

## Slide 65
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 83
Tag: SCL Operated
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220606_124057+seq80toseq84!NotLit.jpg

## Slide 66
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 84
Tag: A/C Unit Failure
Type: Light
Count: 2
Possible: Yes
Comments:
Filename: 20220606_124057+seq80toseq84!NotLit.jpg

## Slide 67
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 85
Tag: A/C Unit A
Type: Digit
Count: 1
Possible: Yes*
Comments: Unit may be off?
Filename: 20220606_124213+seq85!Tempdigit.jpg

## Slide 68
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 85
Tag: A/C Unit B
Type: Digit
Count: 1
Possible: Yes*
Comments: Unit may be off?
Filename: 20220606_124218+seq85!digit not lit.jpg

## Slide 69
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 86
Tag:
Type: Tube
Count: 1
Possible: No
Comments:
Filename: 20220606_124325+seq86.jpg

## Slide 70
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 87
Tag:
Type: Tube
Count: 1
Possible: No
Comments:
Filename: 20220606_124327+seq87.jpg

## Slide 71
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 88
Tag: 11139
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker behind glass
Filename: 20220606_124617+seq88!11139.jpg

## Slide 72
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 89
Tag: 18335
Type: Tube
Count: 1
Possible: No
Comments:
Filename: 20220606_124712+seq89!18335.jpg

## Slide 73
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 89
Tag: 11835
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_124716+seq89!11835.jpg

## Slide 74
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 90
Tag: 11458
Type: Gauge
Count: 1
Possible: Yes*
Comments: High
Filename: 20220606_124814+seq90!11458.jpg

## Slide 75
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 91
Tag: 11457
Type: Gauge
Count: 1
Possible: Yes*
Comments: High
Filename: 20220606_124820+seq91!11457.jpg

## Slide 76
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: Unknown
Tag: 16120
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_125017.jpg

## Slide 77
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 96
Tag: 11138
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_125223+seq96!11138.jpg

## Slide 78
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 97
Tag: 11476
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_125317+seq97!11476.jpg

## Slide 79
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 99
Tag: 18008
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_125409.jpg

## Slide 80
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 100
Tag: 18009
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_125411.jpg

## Slide 81
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 100
Tag: 52001
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_125455+seq100!52001.jpg

## Slide 82
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 101
Tag: 11322
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_125941+seq101!11322.jpg

## Slide 83
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 102
Tag: 11321
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_125930+seq102!11321.jpg

## Slide 84
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 103
Tag: 11320
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_125922+seq103!11320.jpg

## Slide 85
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 105
Tag: 17857
Type: Gauge
Count: 1
Possible: Yes*
Comments: Mask lettering behind glass
Filename: 20220606_130513+seq105!17857.jpg

## Slide 86
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 106
Tag: 18070
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_130522+seq106!18070.jpg

## Slide 87
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 107
Tag: 11293
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_130826+seq107!11293.jpg

## Slide 88
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 108
Tag: 11294
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_130828+seq108!11294.jpg

## Slide 89
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 109
Tag: 11470
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_131028+seq109!11470.jpg

## Slide 90
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 110
Tag: 12203
Type: Gauge
Count: 1
Possible: Yes
Comments:
Need to clean glass
Filename: 20220606_131216+seq110!12203.jpg

## Slide 91
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 111
Tag: 12204
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_131240+seq111!12204.jpg

## Slide 92
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 112
Tag: 11375
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_131303+seq112!11375.jpg

## Slide 93
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 113
Tag: 11376
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_131306+seq113!11376.jpg

## Slide 94
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 114
Tag: 11377
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker behind glass
Filename: 20220606_131309+seq114!11377.jpg

## Slide 95
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 116
Tag: 11215
Type: Gauge
Count: 1
Possible: Yes
Comments:
High
Filename: 20220606_131636+seq116!11215.jpg

## Slide 96
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 117
Tag: 71080
Type: Light
Count: 1
Possible: No
Comments:
Filename: 20220606_131735+seq117!71080.jpg

## Slide 97
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 117
Tag: 71080
Type: Light
Count: 2
Possible: Yes
Comments:
Filename: 20220606_131741+seq117!71080-Power and Safe Lights.jpg

## Slide 98
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 121
Tag: 70405
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132005+seq121!70405.jpg
20220606_132018.jpg

## Slide 99
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 122
Tag: Gas Purity
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132028+seq122!Gas Purity.jpg
20220606_132112.jpg

## Slide 100
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 122
Tag: Gas Purity
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132032+seq122!Gas Purity.jpg

## Slide 101
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 123
Tag: 70405
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132124+seq123!Inches.jpg

## Slide 102
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 124
Tag: 18438
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132214seq124!18438.jpg

## Slide 103
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 125
Tag: 12109
Type: Gauge
Count: 1
Possible: Yes*
Comments: Tape Tail
Filename: 20220606_132335+seq125!12109.jpg

## Slide 104
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 126
Tag: 12110
Type: Gauge
Count: 1
Possible: Yes*
Comments: Tape Tail
Filename: 20220606_132342+seq126!12110.jpg

## Slide 105
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 129
Tag: 11213
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132425+seq129!11213.jpg

## Slide 106
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 130
Tag: 11214
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132427+seq130!11214.jpg

## Slide 107
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 131
Tag: 11565
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132531+seq131!11565.jpg

## Slide 108
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 132
Tag: 11211
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132542+seq132!11211.jpg

## Slide 109
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 137
Tag: BKR133-4
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132727+seq137!BKR133-4.jpg

## Slide 110
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 138
Tag: BKR143-4
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220606_132731+seq138!BKR143-4.jpg

## Slide 111
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 140
Tag: 11402
Type: Gauge
Count: 1
Possible: Yes*
Comments: High
Filename: 20220606_132833+seq140!11402.jpg

## Slide 112
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 141
Tag: O2Pressure
Type: Gauge
Count: 1
Possible: Yes*
Comments: Replace broken gauge
Filename: 20220606_132931+seq141!O2Pressure.jpg

## Slide 113
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 153
Tag: 12438
Type: Gauge
Count: 1
Possible: Yes*
Comments: Need Pic
Filename: NoPic

## Slide 114
SITE WALK REPORT
Site: PI - Unit 1 Turb Bldg
Seq: 143
Tag: 26299
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220606_133010+seq143!26299.jpg

## Slide 115
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 3
Tag: 11663
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075411+seq!11663.jpg

## Slide 116
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 4
Tag: 11655
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075537!11655.jpg

## Slide 117
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 5
Tag: 17410
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075600!17410.jpg

## Slide 118
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 6
Tag: 17408
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075617!17408.jpg

## Slide 119
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 7
Tag: 17411
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075635!17411.jpg

## Slide 120
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 8
Tag: 17409
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075642!17409.jpg

## Slide 121
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 9
Tag: Hour Meter
Type: Digit
Count: 1
Possible: Yes*
Comments: Need Picture
Filename:

## Slide 122
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 10
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075712.jpg

## Slide 123
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 11
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075717.jpg

## Slide 124
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 12
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075728.jpg

## Slide 125
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 13
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075836.jpg

## Slide 126
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 14
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_075930.jpg

## Slide 127
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 16
Tag: 11053
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_080026.jpg

## Slide 128
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 17
Tag:
Type: Gauge
Count: 1
Possible: Yes*
Comments: Loose Glass
Filename: 20220607_080103.jpg

## Slide 129
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 19
Tag: 82231
Type: Thermostat
Count: 1
Possible: Yes*
Comments: WHTM
Filename: 20220607_080400.jpg

## Slide 130
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 20
Tag: 82221
Type: Thermostat
Count: 1
Possible: Yes*
Comments: WHTM
Filename: 20220607_080454.jpg

## Slide 131
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 22
Tag: 12130
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_080607.jpg

## Slide 132
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 23
Tag: 11413
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_080615.jpg

## Slide 133
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 24
Tag: 11414
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_080624.jpg

## Slide 134
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 26
Tag: 18374
Type: Gauge
Count: 1
Possible: Yes*
Comments: Need Picture
Filename: 20220607_081016.jpg

## Slide 135
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 27
Tag: 12131
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_081016.jpg

## Slide 136
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 28
Tag: 12132
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_081020.jpg

## Slide 137
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 29
Tag: 12133
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_081046.jpg

## Slide 138
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 30
Tag: 12134
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_081049.jpg

## Slide 139
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 31
Tag: 12200
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_081219.jpg

## Slide 140
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 32
Tag: 12201
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_081230.jpg

## Slide 141
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 33
Tag: 12135
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_081310.jpg

## Slide 142
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 34
Tag: 12137
Type: Gauge
Count: 1
Possible: Yes*
Comments: Tape tail
Filename: 20220607_081315.jpg

## Slide 143
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 36
Tag: 12138
Type: Gauge
Count: 1
Possible: Yes*
Comments: Tape tail
Filename: 20220607_081533.jpg

## Slide 144
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 37
Tag: 12202
Type: Gauge
Count: 1
Possible: Yes*
Comments: Tape Tail
Filename: 20220607_081623.jpg

## Slide 145
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 38
Tag: 11216
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_081649.jpg

## Slide 146
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 39
Tag: 11217
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_081724.jpg

## Slide 147
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 42
Tag: Victoreen
Type: Light
Count: 19
Possible: Yes*
Comments: Verify Mounting
Filename: 20220607_082037.jpg

## Slide 148
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 43
Tag: GP-1
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220607_082110.jpg

## Slide 149
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 44
Tag: GP-2
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220607_082140.jpg

## Slide 150
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 45
Tag: CD
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220607_082208.jpg

## Slide 151
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 49
Tag: 74060
Type: Light
Count: 40
Possible: Yes
Comments:
Filename: 20220607_082544.jpg

## Slide 152
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 51
Tag: 13-2
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_082827.jpg

## Slide 153
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 52
Tag: 12027
Type: Gauge
Count: 1
Possible: Yes*
Comments: High
Filename: 20220607_083017.jpg

## Slide 154
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 53
Tag: 12028
Type: Gauge
Count: 1
Possible: Yes*
Comments: High
Filename: 20220607_083030.jpg

## Slide 155
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 54
Tag: 12041
Type: Gauge
Count: 1
Possible: Yes*
Comments: High
Filename: 20220607_083117.jpg

## Slide 156
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 55
Tag: 12042
Type: Gauge
Count: 1
Possible: Yes
Comments: High
Filename: 20220607_083226.jpg

## Slide 157
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 56
Tag: 24-7
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_083309.jpg

## Slide 158
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 57
Tag: 81A/B21
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220607_083414.jpg

## Slide 159
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 58
Tag: 81B/B21
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220607_083348.jpg

## Slide 160
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 59
Tag: 81A/B22
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220607_083354.jpg

## Slide 161
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 60
Tag: 81B/B22
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220607_083357.jpg

## Slide 162
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 61
Tag: BKR 211E-6
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_083548.jpg

## Slide 163
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 63
Tag: BKR 121E-19
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_083831.jpg

## Slide 164
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 65
Tag: PI-17738
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_084050.jpg

## Slide 165
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 66
Tag: PI-17739
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_084123.jpg

## Slide 166
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 67
Tag: 5880092
Type: Light
Count: 1
Possible: Yes
Comments:
Filename: 20220607_084221.jpg

## Slide 167
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 69
Tag: 11091
Type: Gauge
Count: 1
Possible: Yes*
Comments: High
Filename: 20220607_084327.jpg

## Slide 168
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 70
Tag: 11460
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_084422.jpg

## Slide 169
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 71
Tag: 11589
Type: Gauge
Count: 1
Possible: Yes
Comments: Remove sticker under glass
Filename: 20220607_084451.jpg

## Slide 170
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 72
Tag: 12207
Type: Gauge
Count: 1
Possible: Yes*
Comments: Need scaffolding
Filename: 20220607_084537.jpg

## Slide 171
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 74
Tag: 16412
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_084942.jpg

## Slide 172
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 88
Tag:
Type: Light
Count: 6
Possible: Yes
Comments:
Filename: 20220607_092318.jpg

## Slide 173
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq:
Tag: 60576
Type: Digit
Count: 2
Possible: Yes
Comments:
Filename: 20220607_092416.jpg

## Slide 174
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 134
Tag: 12208
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_093409.jpg

## Slide 175
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 135
Tag: 11382
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_093450.jpg

## Slide 176
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 136
Tag: 11383
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_093452.jpg

## Slide 177
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 137
Tag: 11384
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove Sticker under glass
Filename: 20220607_093455.jpg

## Slide 178
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 138
Tag: 71090
Type: Light
Count: 2
Possible: Yes
Comments:
Filename: 20220607_093550.jpg

## Slide 179
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 142
Tag: 70515
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_093815.jpg

## Slide 180
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 143
Tag: 70512
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_093856.jpg

## Slide 181
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 144
Tag: 21456
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_093932.jpg

## Slide 182
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 145
Tag: 18439
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_094012.jpg

## Slide 183
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 148
Tag: 11400
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_094137.jpg

## Slide 184
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 149
Tag: 11401
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_094141.jpg

## Slide 185
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 150
Tag: 11566
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_094218.jpg

## Slide 186
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 151
Tag: 11218
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_094235.jpg

## Slide 187
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 154
Tag: 12111
Type: Gauge
Count: 1
Possible: Yes*
Comments: Tape Tail
Filename: 20220607_094316.jpg

## Slide 188
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 155
Tag: 12112
Type: Gauge
Count: 1
Possible: Yes*
Comments: Tape Tail
Filename: 20220607_101620.jpg

## Slide 189
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 158
Tag: BKR 253-21
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_101714.jpg

## Slide 190
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 159
Tag: BKR 263-21
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_101731.jpg

## Slide 191
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 162
Tag: 26300
Type: Digit
Count: 2
Possible: No
Comments: High, more than one reading
Filename: 20220607_101924.jpg

## Slide 192
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 163
Tag: 26300
Type: Digit
Count: 2
Possible: No
Comments: High, more than one reading
Filename: 20220607_101924.jpg

## Slide 193
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 164
Tag: 11388
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_102139.jpg

## Slide 194
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 165
Tag: 11387
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_102141.jpg

## Slide 195
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 166
Tag: 11386
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_102144.jpg

## Slide 196
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 167
Tag: 26314
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_102234.jpg

## Slide 197
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 168
Tag: 26315
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_102238.jpg

## Slide 198
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 169
Tag: 11154
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_102301.jpg

## Slide 199
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 170
Tag: 18734
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_102327.jpg

## Slide 200
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 174
Tag: 12264
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_102606.jpg

## Slide 201
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 175
Tag: 12261
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_102632.jpg

## Slide 202
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 176
Tag: 11152
Type: Gauge
Count: 1
Possible: Yes
Comments: Tape tail (vibrating needle)
Filename: 20220607_102719.jpg

## Slide 203
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 177
Tag: 18733
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_102755.jpg

## Slide 204
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 180
Tag: TC-26312
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_102855.jpg

## Slide 205
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 181
Tag: TC-26313
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_102859.jpg

## Slide 206
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 184
Tag: 11521
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_103033.jpg

## Slide 207
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 186
Tag: 11684
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_103239.jpg

## Slide 208
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 187
Tag: 18502
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_103311.jpg

## Slide 209
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 188
Tag: BKR 221E-7
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_103709.jpg

## Slide 210
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 190
Tag: BKR111E-2
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_103853.jpg

## Slide 211
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 197
Tag: 1321
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_104123.jpg

## Slide 212
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 202
Tag: 12219
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_104248.jpg

## Slide 213
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 203
Tag: 1324
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_104255.jpg

## Slide 214
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 205
Tag: 11115
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_104330.jpg

## Slide 215
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 208
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_104533.jpg

## Slide 216
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 213
Tag: 1322
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_104821.jpg

## Slide 217
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 218
Tag: 12221
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_104918.jpg

## Slide 218
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 219
Tag: 1325
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_104935.jpg

## Slide 219
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 221
Tag: 11116
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_104957.jpg

## Slide 220
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 226
Tag: 11117
Type: Gauge
Count: 1
Possible: Yes*
Comments: Remove sticker under glass
Filename: 20220607_105242.jpg

## Slide 221
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 227
Tag: 1323
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_105319.jpg

## Slide 222
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 232
Tag: TI-12223
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_105501.jpg

## Slide 223
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 233
Tag: TI-1326
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_105504.jpg

## Slide 224
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 236
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_105639.jpg

## Slide 225
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 242
Tag: 12128
Type: Gauge
Count: 1
Possible: Yes*
Comments: High
Filename: 20220607_105830.jpg

## Slide 226
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 257
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_110248.jpg
20220607_110307.jpg

## Slide 227
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 260
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_110329.jpg

## Slide 228
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 261
Tag:
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_110511.jpg

## Slide 229
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 262
Tag:
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_110516.jpg

## Slide 230
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 263
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_110530.jpg

## Slide 231
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 266
Tag:
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_110609.jpg

## Slide 232
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 267
Tag:
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_110611.jpg

## Slide 233
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 268
Tag:
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_110629.jpg

## Slide 234
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 294
Tag: 5885023
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_111831.jpg

## Slide 235
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 297
Tag: 5885123
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_111834.jpg

## Slide 236
SITE WALK REPORT
Site: PI - Unit 2 Turb Bldg
Seq: 304
Tag: 2TI-5020
Type: Digit
Count: 1
Possible: Yes*
Comments: display off
Filename: 20220607_112407.jpg

## Slide 237
SITE WALK REPORT – D5-D6
Site: PI – D5/D6
Seq: 1
Tag: 2TI-5156
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_112726.jpg

## Slide 238
SITE WALK REPORT
Site: PI – D5/D6
Seq: 2
Tag: 2TI-5167
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_112737.jpg

## Slide 239
SITE WALK REPORT
Site: PI – D5/D6
Seq: 3
Tag: 2TI-5209
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_112743.jpg

## Slide 240
SITE WALK REPORT
Site: PI – D5/D6
Seq: 4
Tag: 2TI-5656
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_113119.jpg

## Slide 241
SITE WALK REPORT
Site: PI – D5/D6
Seq: 5
Tag: 2TI-5667
Type: Gauge
Count: 1
Possible: Yes
Comments: Wrong Picture
Filename: 20220607_113124.jpg

## Slide 242
SITE WALK REPORT
Site: PI – D5/D6
Seq: 6
Tag: 2TI-5709
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_113127.jpg

## Slide 243
SITE WALK REPORT
Site: PI – D5/D6
Seq: 7
Tag: 2TI-5709
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_113127.jpg

## Slide 244
SITE WALK REPORT
Site: PI – D5/D6
Seq: 9
Tag: 2TI-5020
Type: Gauge
Count: 1
Possible: Yes
Comments: Mising Pic
Filename: 20220607_113127.jpg

## Slide 245
SITE WALK REPORT
Site: PI – D5/D6
Seq: 38
Tag: 2TI-6156
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_113411.jpg

## Slide 246
SITE WALK REPORT
Site: PI – D5/D6
Seq: 39
Tag: 2TI-6167
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_113413.jpg

## Slide 247
SITE WALK REPORT
Site: PI – D5/D6
Seq: 40
Tag: 2TI-6209
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_113417.jpg

## Slide 248
SITE WALK REPORT
Site: PI – D5/D6
Seq: 41
Tag: 2TI-6656
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_113501.jpg

## Slide 249
SITE WALK REPORT
Site: PI – D5/D6
Seq: 42
Tag: 2TI-6667
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_113503.jpg

## Slide 250
SITE WALK REPORT
Site: PI – D5/D6
Seq: 43
Tag: 2TI-6709
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_113506.jpg

## Slide 251
SITE WALK REPORT
Site: PI – D5/D6
Seq: 46
Tag: 2TI-6020
Type: Digit
Count: 1
Possible: Yes
Comments:
Filename: 20220607_113530.jpg

## Slide 252
SITE WALK REPORT
Site: PI – D5/D6
Seq: 63
Tag: TI-12367
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220607_114053.jpg

## Slide 253
SITE WALK REPORT
Site: PI – Condensate Pump Rm
Seq: Condensate Pump Room
Tag: PI-1024B
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220608_155506.jpg

## Slide 254
SITE WALK REPORT
Site: PI – Condensate Pump Rm
Seq: Condensate Pump Room
Tag: PI-1285
Type: Gauge
Count: 1
Possible: Yes
Comments:
Filename: 20220608_155606.jpg